## A
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## B
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## C
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## D
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## E
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## F
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## G
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## H
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## I
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## J
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## K
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## L
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## M
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## N
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## O
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL

## P
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS -->
BACNET OBJECT FLOOR -->
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 |  | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | [9 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 |  | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 |  | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 |  | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | [9 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | [9 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 |  | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | [9 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | [9 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | [9 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | [9 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | [9 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | [9 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | [9 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | [9 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | [9 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | [9 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | [9 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | [9 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | [9 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | [9 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | [9 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 |  | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | [9 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | [9 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | [9 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | [9 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | [9 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | [9 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | [9 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 |  | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | [9 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | [9 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | [9 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | [9 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | [9 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | [9 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | [9 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 |  | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | [9 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | [9 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 |  | Modbus Device Address |  |  | unit16 | R/W |  | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | [9 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 |  | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 |  | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 |  | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | [9 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | [9 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | [9 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 |  | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 |  | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 |  | IP Address |  |  | string(8) | R/W |  | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | [9 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 |  | Netmask |  |  | string(8) | R/W |  | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | [9 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | [9 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | [9 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | [9 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | [9 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | [9 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 |  | Gateway |  |  | string(8) | R/W |  | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | [9 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | [9 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 |  | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | [9 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 |  | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | [9 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | [9 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | [9 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 |  | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | [10 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 |  | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 |  | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 |  | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | [9 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | [9 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 |  | Interface baud rate in bits per second |  |  | uint32 | R/W |  | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | [9 empty] | system |  |  | ALL
SERIAL BITS | 1133 |  | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 |  | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 |  | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 |  | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 |  | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 |  | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 |  | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 |  | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 |  | Current Avg Element | A | Metrology | float32 | R |  | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | [9 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 |  | Current CH1 (A) | A | Metrology | float32 | R |  | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | [9 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 |  | Current CH2 (B) | A | Metrology | float32 | R |  | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | [9 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 |  | Current CH3 (C) | A | Metrology | float32 | R |  | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | [9 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 |  | Voltage L to N Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | [9 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 |  | Voltage L1 to N (AN) | V | Metrology | float32 | R |  | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | [9 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 |  | Voltage L2 to N (BN) | V | Metrology | float32 | R |  | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | [9 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 |  | Voltage L3 to N (CN) | V | Metrology | float32 | R |  | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | [9 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 |  | Voltage L to L Avg Element | V | Metrology | float32 | R |  | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | [9 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 |  | Voltage L1 to L2 (AB) | V | Metrology | float32 | R |  | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | [9 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 |  | Voltage L2 to L3 (BC) | V | Metrology | float32 | R |  | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | [9 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 |  | Voltage L3 to L1 (CA) | V | Metrology | float32 | R |  | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | [9 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 |  | Line Frequency | Hz | Metrology | float32 | R |  | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | [9 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 |  | Power Sum Element | kW | Metrology | float32 | R |  | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | [9 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 |  | Power CH1 (A) | kW | Metrology | float32 | R |  | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | [9 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 |  | Power CH2 (B) | kW | Metrology | float32 | R |  | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | [9 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 |  | Power CH3 (C) | kW | Metrology | float32 | R |  | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | [9 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 |  | VA Sum Element | kVA | Metrology | float32 | R |  | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | [9 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 |  | VA CH1 (A) | kVA | Metrology | float32 | R |  | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | [9 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 |  | VA CH2 (B) | kVA | Metrology | float32 | R |  | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | [9 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 |  | VA CH3 (C) | kVA | Metrology | float32 | R |  | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | [9 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 |  | VAR Sum Element | kVAr | Metrology | float32 | R |  | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | [9 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 |  | VAR CH1 (A) | kVAr | Metrology | float32 | R |  | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | [9 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 |  | VAR CH2 (B) | kVAr | Metrology | float32 | R |  | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | [9 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 |  | VAR CH3 (C) | kVAr | Metrology | float32 | R |  | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | [9 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 |  | Apparent PF Avg Element | PF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | [9 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 |  | Apparent PF CH1 (A) | PF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | [9 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 |  | Apparent PF CH2 (B) | PF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | [9 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 |  | Apparent PF CH3 ( C) | PF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | [9 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 |  | Exported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | [9 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 |  | Exported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | [9 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 |  | Exported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | [9 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 |  | Exported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | [9 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 |  | Imported Energy Sum Element | kWh | Metrology | float32 | R |  | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | [9 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 |  | Imported Energy CH1 (A) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | [9 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 |  | Imported Energy CH2 (B) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | [9 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 |  | Imported Energy CH3 (C) | kWh | Metrology | float32 | R |  | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | [9 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 |  | Exported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | [9 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 |  | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | [9 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 |  | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | [9 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 |  | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | [9 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 |  | Imported VAh Sum Element | kVAh | Metrology | float32 | R |  | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | [9 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 |  | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | [9 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 |  | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | [9 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 |  | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R |  | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | [9 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 |  | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 |  | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 |  | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | [9 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 |  | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | [9 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 |  | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 |  | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 |  | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | [9 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 |  | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | [9 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 |  | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 |  | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 |  | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | [9 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 |  | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | [9 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 |  | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 |  | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 |  | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | [9 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 |  | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R |  | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | [9 empty] | element |  |  | ALL
Events MSW | 1263 |  | Events MSW |  |  | bitfield32 | R |  | AI | Events | system |  |  | ALL
Events LSW | 1264 |  | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 |  | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 |  | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
USER COMMAND POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 |  | Reset (software) processor |  | User | unit16 | W |  | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 |  | Clear all accumulated measurements (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 |  | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W |  | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 |  | Clear Peak Demand Element |  | User | unit16 | W |  | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 |  | Clear Peak Demand All |  | User | unit16 | W |  | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 |  | Reset to User Defaults |  | User | unit16 | W |  | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 |  | Sliding or Fixed |  | Config | enum16 | R |  | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 |  | Demand Window | Min | Config | uint16 | R |  | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 |  | Volt Multiplier VINPUT1 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | [9 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 |  | Volt Multiplier VINPUT2 |  | Config | float32 | R/W |  | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | [9 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 |  | Service Type |  | Config | enum16 | R/W |  | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 |  | Snap MV Threshold | PER | Config | float32 | R/W |  | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | [9 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 |  | Snap Rog Threshold | PER | Config | float32 | R/W |  | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | [9 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 |  | Snap Volt Threshold | V | Config | float32 | R/W |  | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | [9 empty] | system |  |  | ALL
Communications Mode | 2214 |  | Communications Mode |  | Config |  |  |  | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 |  | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W |  | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | [9 empty] | system |  |  | ALL
Voltage Input Element | 2217 |  | Element Voltage Input |  | Config | enum16 | R/W |  | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 |  | CT1 RANGE | A | Config | float32 | R/W |  | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | [9 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 |  | Voltage Reference for CT1 |  | Config | enum16 | R/W |  | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 |  | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | [9 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 |  | CT1 TYPE |  | Config | enum16 | R/W |  | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 |  | CT1 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | [9 empty] | element |  |  | ALL
CH1 CT Sign | 2226 |  | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W |  | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 |  | CT2 RANGE | A | Config | float32 | R/W |  | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | [9 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 |  | Voltage Reference for CT2 |  | Config | enum16 | R/W |  | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 |  | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | [9 empty] | element | >0 |  | ALL
CH2 CT type | 2232 |  | CT2 TYPE |  | Config | enum16 | R/W |  | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 |  | CT2 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | [9 empty] | element |  |  | ALL
CH2 CT Sign | 2235 |  | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W |  | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 |  | CT3 INTEGER | A | Config | float32 | R/W |  | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | [9 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 |  | Voltage Reference for CT3 |  | Config | enum16 | R/W |  | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 |  | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W |  | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | [9 empty] | element | >0 |  | ALL
CH3 CT type | 2241 |  | CT3 TYPE |  | Config | enum16 | R/W |  | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 |  | CT3 PHASE SHIFT | Deg | Config | float32 | R/W |  | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | [9 empty] | element |  |  | ALL
CH3 CT Sign | 2244 |  | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W |  | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 |  | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 |  | PF Sign Convention |  | Config | uint16 | R/W |  | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 |  | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 |  | BACnet UDP Port |  | Config | uint16 | R/W |  | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 |  | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 |  | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | [9 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 |  | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | [12 empty] | ALL
BACnet Max Info Frames | 2262 |  | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 |  | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 |  | BBMD IP Address |  | Config | string(16) | R/W |  | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | [10 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | [10 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 |  | LCD/WebApp Read Password |  | Config | uint16 | R/W |  | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 |  | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 |  | Customer Line frequency |  | Config | float | R/W |  | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | [11 empty] | Reserved | ALL
Communications Interface Configured | 2276 |  | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 |  | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 |  | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 |  | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 |  | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | [12 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 |  | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | [12 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 |  | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 |  | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 |  | Displacement PF Avg Element | dPF | Metrology | float32 | R |  | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | [12 empty] | ALL
Displacement PF CH1 (MSW) | 2302 |  | Displacement PF CH1 (A) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | [12 empty] | ALL
Displacement PF CH2 (MSW) | 2304 |  | Displacement PF CH2 (B) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | [12 empty] | ALL
Displacement PF CH3 (MSW) | 2306 |  | Displacement PF CH3 (C) | dPF | Metrology | float32 | R |  | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | [12 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 |  | Avg Apparent PF Element | aPF | Metrology | float32 | R |  | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | [12 empty] | ALL
Apparent PF CH1 (MSW) | 2310 |  | Apparent PF CH1 (A) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | [12 empty] | ALL
Apparent PF CH2 (MSW) | 2312 |  | Apparent PF CH2 (B) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | [12 empty] | ALL
Apparent PF CH3 (MSW) | 2314 |  | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R |  | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | [12 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 |  | Distortion PF Avg Element | tPF | Metrology | float32 | R |  | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | [12 empty] | ALL
Distortion PF CH1 (MSW) | 2318 |  | Distortion PF CH1 (A) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | [12 empty] | ALL
Distortion PF CH2 (MSW) | 2320 |  | Distortion PF CH2 (B) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | [12 empty] | ALL
Distortion PF CH3 (MSW) | 2322 |  | Distortion PF CH3 (C) | tPF | Metrology | float32 | R |  | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | [12 empty] | ALL
THD Avg Element (MSW) | 2324 |  | THD Avg Element | % | Metrology | float32 | R |  | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | [12 empty] | ALL
THD CH1 (MSW) | 2326 |  | THD CH1 (A) | % | Metrology | float32 | R |  | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | [12 empty] | ALL
THD CH2 (MSW) | 2328 |  | THD CH2 (B) | % | Metrology | float32 | R |  | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | [12 empty] | ALL
THD CH3 (MSW) | 2330 |  | THD CH3 (C) | % | Metrology | float32 | R |  | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | [12 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 |  | Power Demand Max Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | [12 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 |  | Power Demand This Interval Element | kW | Metrology | float32 | R |  | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | [12 empty] | ALL
VA Peak Demand Element (MSW) | 2336 |  | VA Demand Max Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | [12 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 |  | VA Demand This Interval Element | kVA | Metrology | float32 | R |  | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | [12 empty] | ALL
Not Used | 2340 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 |  | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 |  | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 |  | Energy Net Sum Element | kWh | Metrology | float32 | R |  | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | [9 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 |  | Energy Net CH1 | kWh | Metrology | float32 | R |  | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | [9 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 |  | Energy Net CH2 | kWh | Metrology | float32 | R |  | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | [9 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 |  | Energy Net CH3 | kWh | Metrology | float32 | R |  | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | [9 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 |  | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 |  | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 |  | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | [9 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 |  | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R |  | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | [9 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 |  | VARh Net Sum Element | kVArh | Metrology | float32 | R |  | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 |  | VARh Net CH1 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 |  | VARh Net CH2 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | [9 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 |  | VARh Net CH3 | kVArh | Metrology | float32 | R |  | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | [9 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 |  | Time Since Reset MSW | Sec | Metrology | uint32 |  |  | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 |  | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 |  | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 |  | CH1 Angle | Deg | Metrology | float32 | R |  | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | [9 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 |  | CH2 Angle | Deg | Metrology | float32 | R |  | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | [9 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 |  | CH3 Angle | Deg | Metrology | float32 | R |  | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | [12 empty] | ALL
Phase Chek System Status | 2377 |  | System Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Phase Check System Status | system | 0-16 | Modbus registers are little-endian (ie Element A is bit 0, Element B is bit 1…Element P is bit 15) BACnet is big-endian (ie Element A is bit 15, Element B is bit 14….Element P is bit 0) | ALL
Phase Chek Element Status | 2378 |  | Element Phase Check Status |  | Metrology | bitfield16 | R |  | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 |  | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 |  | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 |  | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 |  | Element Angle |  | Metrology | float | R |  | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | [12 empty] | ALL
PULSE INPUTS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 |  | Pulse Input 1 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 |  | Pulse Input 1 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 |  |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 |  | Pulse Input 1 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 |  | Pulse Input 1 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 |  | Pulse Input 1 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 |  | Pulse Input 2 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 |  | Pulse Input 2 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | [5 empty] | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 |  | Pulse Input 2 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 |  | Pulse Input 2 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | [5 empty] | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 |  | Pulse Input 2 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 |  | Pulse Input 3 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 |  | Pulse Input 3 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 |  | Pulse Input 3 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 |  | Pulse Input 3 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 |  | Pulse Input 3 Accumulator Clear |  | User |  | W |  | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 |  | Pulse Input 4 Enable |  | Config | uint16 | R/W |  | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 |  | Pulse Input 4 Scale Factor |  | Config | float32 | R/W |  | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | [5 empty] | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 |  | Pulse Input 4 Units |  | Config | string(4) | R/W |  | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 |  |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 |  |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 |  | Pulse Input 4 Accumulator |  | Metrology | float32 | R |  | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | [5 empty] | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 |  | Pulse Input 4 Accumulator Clear |  | User | unit16 | W |  | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - |  | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 |  | State of Alarm |  | Metrology | uint16 | R/W |  | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 |  | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 |  | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 |  | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 |  | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 |  | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 |  | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 |  | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 |  | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W |  | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
| 2460 |  | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
| 2462 |  | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
| 2464 |  | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
| 2466 |  | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
| 2468 |  | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
| 2470 |  | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
| 2472 |  | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2474 |  | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2476 |  | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2478 |  | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2480 |  | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 |  | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
| 2482 |  | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W |  | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 |  | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 |  | Voltage Alarm Persistence | Sec | Config | uint16 | R/W |  | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 |  | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 |  | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 |  | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R |  | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 |  | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 |  | Real Time Clock MSW |  | Config | uint16 | R/W |  | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 |  | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - |  | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 |  | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 |  | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 |  | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 |  | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 |  | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 |  | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 |  | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 |  | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 |  | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 |  | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 |  | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 |  | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 |  | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 |  | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 |  | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 |  | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 |  | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 |  | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 |  | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 |  | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 |  | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 |  | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 |  | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 |  | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 |  | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 |  | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 |  | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 |  | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 |  | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 |  | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 |  | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 |  | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 |  |  |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | [11 empty] | 2 Char |  | ALL
BACnet Description 2 | [11 empty] | 2 Char |  | ALL
BACnet Description 3 | [11 empty] | 2 Char |  | ALL
BACnet Description 4 | [11 empty] | 2 Char |  | ALL
BACnet Description 5 | [11 empty] | 2 Char |  | ALL
BACnet Description 6 | [11 empty] | 2 Char |  | ALL
BACnet Description 7 | [11 empty] | 2 Char |  | ALL
BACnet Description 8 | [11 empty] | 2 Char |  | ALL
BACnet Description 9 | [11 empty] | 2 Char |  | ALL
BACnet Description 10 | [11 empty] | 2 Char |  | ALL
BACnet Description 11 | [11 empty] | 2 Char |  | ALL
BACnet Description 12 | [11 empty] | 2 Char |  | ALL
BACnet Description 13 | [11 empty] | 2 Char |  | ALL
BACnet Description 14 | [11 empty] | 2 Char |  | ALL
BACnet Description 15 | [11 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL